48501 DOOR INTERLOCK CONTROLLER

- GENERAL

  - SUMMARY

    - Section includes specifications for a site configurable PLC controller for operating door interlock systems of up to five doors.

  - RELATED REQUIREMENTS

    - MasterFormat 2014

      - 08 71 00 - Door Hardware

        - 08 71 06 – Door Hardware Schedule

      - 28 05 00 – Common Work Results

        - 28 05 13 – Conductors and Cables for Electronic Safety and Security

        - 28 05 13.16 – Access Control Conductors and Cables

      - 28 06 10 – Schedules for Electronic Access Control and Intrusion Detection

      - 28 10 10 – Electronic Access Control and Intrusion Detection

    - MasterFormat 2016

      - 08 71 00 - Door Hardware

        - 08 71 06 – Door Hardware Schedule

      - 27 15 01 – Communications Horizontal Cabling Applications

        - 27 15 01.11 – Conductors and Cables for Electronic Safety and Security

        - 27 15 01.15 – Access Control Communications Conductors and Cables

      - 28 05 07 – Power Sources for Electronic Safety and Security

        - 28 05 07.11 – Power Sources for Access Control

      - 28 06 10 – Schedules for Access Control

      - 28 10 00 -  Access Control

        - 28 14 00 - Access Control System Hardware

        - 28 15 00 - Access Control Hardware Devices

        - 28 16 00 - Access Control Interfaces

  - REFERENCES

    - Abbreviations

      - PLC – Programmable Logic Controller

      - REX – Request to Exit

    - Reference Standards

      - ADA – Americans with Disabilities Act

      - NFPA 70 – National Electric Code

      - NFPA 72 – National Fire Alarm Code

      - NFPA 101 – Life Safety Code

      - NFPA 731 – Guide for Premises Security

      - OSHA – Occupational Safety and Health Act

      - UL 294 – Standard for Access Control Systems

      - BHMA A156.18 – American National Standard for Materials and Finishes

      - State and Local Building Codes

  - QUALITY ASSURANCE

    - Manufacturer Qualifications:

      - Minimum of ten years of experience in manufacture and design of electronic access control hardware and devices.

      - Capable of providing equipment for expansions, replacements, and spare parts.

      - Capable of providing factory direct technical support.

      - Products shall be manufactured in the United States of America.

  - INSTALLER QUALIFICATIONS

    - Minimum of five years of experience installing access control, surveillance and security systems and devices.

  - SUBMITTALS

    - Submit in accordance with Division 01, Section 01 33 00

    - Product Data:

      - Manufacturer’s standard details and catalog information demonstrating compliance with the Project Documents.

      - Data sheets marked to identify specific products and accessories necessary for a complete system.

      - Installation Instructions.

    - Close-Out Submittals

        - User manual.

        - System device locations on architectural floor plans.

        - Wiring and connection diagram.

        - Maintenance requirements.

        - Written system test report.

  - PRODUCT HANDLING AND STORAGE

    - Store products indoors in a secured area, and protect from moisture, construction traffic, and damage.

    - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer.

  - WARRANTY

    - All equipment, materials, and labor shall have a limited warranty of 12 months from the date of final acceptance by the Owner.

    - Software maintenance updates or upgrades shall be provided at no additional cost to the Owner during the warranty period.

- PRODUCTS

  - MANUFACTURER

    - Dortronics Systems, Inc.

1668 Sag Harbor Turnpike

Sag Harbor, NY  11963

800-906-0137

www.dortronics.com

    - Product Model:	Model 48501

      - No Alternates

  - DESCRIPTION

    - The Door Interlock Controller (“Door Controller”) shall have the following characteristics:

      - Interoperable with all commercial access control systems.

      - Field Configurable

      - Door control capability:  Two (2) to Five (5) doors

      - Enclosure:  12”x15-1/2”x4-1/2” steel NEMA 1 enclosure

        - Integral Power Supply:  4 amps 12/24 VDC

        - Fire Alarm connection for Emergency Egress

      - Electrical:

        - AC Input: Fused 110 VAC.

        - UL 294 Class 2 DC Output: 4 amp @ 12/24 VDC (field selectable).

        - Signal Inputs:

            - Door status:  Five (5)

            - REX status:  Five (5)

            - Panic Release:  One (1)

            - Interlock/Shunt Override:  One (1)

        - Control Outputs:

          - Lock Output Relays:  Five (5) rated for 2 amps @ 28 VDC

          - Door Status:  Five (5)

          - LED Traffic Light Indicators:  Ten (10) (two for each door)

          - Door Alarm:  One (1)

          - Panic Release:  One (1)

  - OPERATION

    - The Door Controller shall be configured to operate as follows:

      - Only designated doors shall be unlocked or open at the same time.

      - Unlocking or opening one door shall automatically secure other designated doors within the Interlock.

      - A request for access at any normally locked door will inhibit the REX inputs for all other locked doors and secure all designated unlocked doors in the area.

      - Lock relay contacts to switch low voltage power to maglocks and/or strikes.

      - Lock outputs settable for either wet or dry contacts and fail-safe or fail-secure operation.

      - For user feedback, designated red/green LED outputs shall be field selectable for either lock status or door availability status.

      - Two designated alarm outputs:

        - Interlock door violation alarm.

        - Emergency unlock for a panic release.

      - Other available customized operations selectable to allow adjustable timed sequences for:

        - Setting emergency unlock time.

        - System pause (usually to allow airlock pressure to equalize).

        - Propped open door alarm time.

  - ACCESSORIES

    - The manufacturer shall have available the following accessories to support system installation and operation:

      - 1100 Series Electromagnetic Door Locks

      - 3300 Series Electric Strikes

      - 3400 Series Electric Drop Bolts

      - 5210 Series Mushroom & Key Reset Buttons

      - 5276 WR Series Waterproof Switches

      - 5277 Series Piezoelectric Switches

      - 5278 Series Touchless Switches

      - 5287 Series Heavy Duty Buttons

      - 6500 Series Emergency Pull Stations

      - 7201 Series Hi-Intensity LED’s

      - 7286 Series Door Prop & Exit Alarms

      - 7000 Series Annunciators & Controls

- EXECUTION

  - EXAMINATION

    - Examine conditions and proceed with work in accordance with Division 01, Section 01 71 00.

    - Notify of any adverse conditions affecting installation or subsequent operation.

    - Installation location per drawings.

      - Notify Owner if selected location is not secure or does not offer protection from accidental damage.

      - Notify Owner if location does not provide reasonable temperature and humidity conditions, free from sources of electrical and electromagnetic interference.

  - INSTALLATION

    - Installation shall be accomplished in a professional manner by qualified personnel meeting Installer requirements.

    - Install necessary wiring in accordance with manufacturer's recommendations.

    - All wiring shall be installed in accordance with NFPA 70, the National Electrical Code.

    - Install controllers and devices in accordance with manufacturer's instructions at locations indicated in the plans.

    - Configure interlock controls for proper door sequencing as described in the Contract Documents.

    - Install products under environmental conditions within Manufacturer's published limits.

  - FIELD QUALITY CONTROL

    - Testing

      - Check tightness of all terminal strip wire clamping screws and circuit board mounting screws.

      - Test proper operation of door interlock controllers and connected components of the system.

      - Determine and report all problems to the Manufacturer.

    - Installation Contractor shall submit a written test report that the system has been 100% tested and approved.

      - Final test shall be witnessed by the Owner, Engineer, Electrical Contractor, Chief Security Officer, and performed by the Installation Contractor.

      - Final test report shall be included in the Close-out Submittal package.

    - Training

      - Provide instruction to the Owner's satisfaction with regard to proper use and operation of the system.

  - ADJUSTING

    - Make proper adjustment to controller, extensions and readers for correct operation in accordance with manufacturer's instructions.

  - DEMONSTRATION

    - Demonstrate at final inspection that Door Interlock control system and associated ancillary devices function properly.

END OF SECTION